INSTRUCTIONS FOR UPGRADING A 28 PT MICRO PLC WITH VERSION 2.01, 2.02, 3.00 or 3.01

FIRMWARE [IN SYSTEM UPGRADE TO VERSION 3.10]

The Micro PLCs have their operating firmware stored in FLASH memory as opposed to EPROM’s.  The firmware upgrade for these boards is provided on floppy disk. The PC Loader utility controls downloading the new firmware from the floppy to the FLASH memory.  This utility requires an IBM AT/PC compatible computer with at least 640K ram, one floppy drive, MSDOS 3.3 (or higher),and one RS232 serial port. This utility functions optimally with a hard drive with at least 1 meg available space.

TO INSTALL THE NEW FIRMWARE, PERFORM THE FOLLOWING STEPS:

1. Save or backup any programs or data resident in the Micro PLC before performing the update function.

2. Place the Micro PLC in STOP/NO IO mode.

3. Connect the serial port of your computer (master) to serial port 1 (left-most port) on the 28 or 23 point Micro PLC to be updated (slave).  Use a standard LM90 cable and RS232/RS422 converter.(GEF part numbers for cables and converters are at the end of this document.) The Micro Serial Port must be set to a buad rate of 19200 (which

is the default setting).

4. Insert the supplied floppy disk , labeled 44A737812-G06, into your A: or B: drive.

5. At the A:\> prompt (or B:\> prompt), type update.

6. From the main menu, press the F1 key to attach to the slave device.

7. Once the slave device is attached, the boot mode menu will appear - press F1 to enter BOOT MODE and press the 'Y' key to confirm the operation. The OK and RUN LED’s on the front of the power supply should now be flashing in unison.

8. Once in boot mode, a new menu will be displayed allowing the baud rate to be changed from the initial baud rate, if desired. To change the baud rate, press the F2 key. Press the TAB key to toggle through the supported baud rates then press the ENTER key to change the baud rates of both the master and the slave. The Micro PLC can be loaded at 38,400 baud, if your computer supports that baud rate.

9. When the baud rate change operation is complete, press the F1 key to download the new firmware.

10. Press the 'Y' key to confirm the operation. The download will take between several minutes and several hours depending on the module being upgraded and the selected baud rate.

11. When the download is complete , the PC loader will instruct you to power cycle your Micro PLC. At this time, power cycle the Micro PLC.  NOTE:  DO NOT TURN OFF PLC POWER WHILE POWERING BACK UP. (The PLC will flash its RUN LED, then turn it off, then flash the RUN LED again.  It will then return to boot mode (OK and RUN LEDs will flash).  At this point,  press any key to continue, as instructed by the update utility.  Then press a key again, as instructed by the update utility.

12.  You should now repeat steps 6, 8-10.

- Place the label in the kit which says “UPDATED TO Firmware Version 3.10” next to the product label on

the Micro PLC unit.

PART NUMBERS FOR GE FANUC CABLES AND RS232/422 CONVERTERS

GEF/Horner Mini Converter with cable	IC690ACC901

25 Pin RS232 Serial Cable			IC690CBL705

9 Pin RS232 Serial Cable			IC690CBL702

RS422 15 pin Cable			IC690CBL303

GEF Converter (requires cables above)	IC690ACC900